Module 10:

Bulk Storage Facility/Tank Farm Simulation Exercise

Objective

Upon completing the module, you will be able to effectively manage an incident at a bulk storage facility/tank farm.

Methodology

This module uses lecture, discussion, and a simulation exercise.

NFPA 1021 Standards Cross-Reference Matrix

3-6, 3-7, 4-6, 4-7

Introduction

The need for specialized technical advice and multi-agency involvement places bulk storage facilities in the target hazard class.

In this module, you will learn about tank farm characteristics, types of tank farm fires, firefighting strategies, the proper formula for foam application, and resources requirements.

Open Floating Roof Tanks

Characteristics

A 360 wind girder around the top portion of the tank shell provides stability for the tank shell. The thickest portion of the tank is at the bottom, while the thinnest portion is at the top. A stairway provides access from ground level, and a heat shield is provided for protection. The foam outlet provided at the top of the stairs is protected by a heat shield and is pressurized from ground level.

The foam piping system permits foam to be applied to seal the area from ground level. The floating roof is separated from the tank shell by either a panograph arrangement or a neoprene seal. This seal is protected by a fabric or metal weather shield. New tanks have a double seal to reduce emissions; this double seal, however, makes a fire inaccessible and more difficult to extinguish.

Floating roofs have drains that can be opened to drain excess water from the roof. Stairs are available to access the roof and wind girder. The roof has vents and manway access points. (Breathing apparatus is required. This is an IDLH.) A drain valve from the roof drain is located at the bottom of the tank to drain excess water from the tank roof.

Certain open floating roof tanks are constructed with geodetic tops as a protective covering. These coverings are made of lightweight metal designed to burn away quickly under fire conditions. They provide additional protection against the weather.

Fires

Most fires occur around the weather shield area and tank shell. These fires can be extinguished from the wind girder, from the top of the stairs, or from the floating roof. Breathing apparatus must always be worn. When large portions of the seal area are involved, it is preferable to have at least two hose streams working around the wind girder, in opposite directions. Most wind girders do not have a railing; be careful when working from these girders. If a fire is burning beneath the stairs and prevents access, use portable towers, foam monitors, or streams from elevated platforms. Exercise caution so that excessive amounts of foam do not flow onto the roof, resulting in the roof sinking. An observer should be watching applications closely. If a seal has been burning for a long period, apply cooling water to the outside of the tank shell. The need to use cooling water will be indicated by blistering or discoloring of the shell paint. Avoid directing large, straight streams of foam or water onto the flammable product at the damaged roof seal; this could intensify the fire. Good foam-aspirating nozzles are needed, regardless of the type of foam used. When foam is delivered from grade level, it is difficult to get sufficient foam into the annular space. Foam has a tendency to flow onto the roof. In this event, immediately open the roof drains to reduce the possibility of sinking the roof. Monitor the drain valve area for product release. If the roof sinks, there will be complete involvement of the entire liquid surface. Flammable liquids are normally stored in these types of tanks.

Covered Floating Roof Tanks

Characteristics

- Covered floating tanks have an internal floating roof/pan.

- A cone roof is identified by exterior vents (eyebrows).

- Cone roofs have a weak seal-to-roof joint.

- The roof is designed to separate from the shell joint in the event of an ignition source and explosion.

- The roof can remove itself in one piece or in fragments, and its parts can travel a considerable distance.

- Flammable liquids are normally stored in these types of tanks. Flashpoint is below 100F (37.8C).

- An internal foam system is delivered through fixed foam chambers.

Fires

These tanks usually do not hold an ignitable mixture, except during periods of initial fill and up to 18 to 25 hours thereafter. Seal or rim fires are virtually impossible to fight in a covered roof tank with portable fire extinguishing equipment. Side vents are too small to permit access with foam streams directed from ground level. On some occasions, cone roofs have blown off, thus involving the entire surface area. If this occurs, the floating roof or pan may sink, and the fire should be treated as a cone roof fire and extinguished by monitor nozzles or other topside applications. Subsurface injection is not recommended since the roof, either afloat or in a sunken state, could obstruct foam travel to the tank surface.

Cone Roof Tanks

Characteristics

Cone roof tanks have no floating roofs. They appear similar to covered floating roof tanks; however, there are no external side vents at the top of each tank. These tanks have a vapor space between the liquid and the underside of the roof. If this vapor space is in the explosive range and an ignition source is introduced, an explosion will occur. The roof may separate from the shell joint if an explosion occurs. It may separate in one piece, or fragments could travel a considerable distance. At other times, it may fall back into the tank or remain intact. Current standards dictate that only combustible liquids be stored in these tanks, but such is not always the case. Consider foam application from internal foam chambers, if available.

Fires

Fires normally involve the entire surface area of the tank. Consider two extinguishment options:  topside and subsurface. If a fire involves a polar solvent, the extinguishment technique is limited to topside application with alcohol-resistant foams only. When topside application is indicated for hydrocarbon fuels, use fixed-foam systems, foam towers, high-capacity monitor nozzles, or elevated platform devices.

Tank Vent Fires

Fires burning in pressure vacuum vents (PVVs) with a yellow or orange flame and emitting black smoke indicate that the vapor/air mixture in the tank is above flammable or explosive limits. This type of fire can be extinguished readily with dry chemical. Fire burning in a tank vent with a snapping blue-red, nearly smokeless flame indicates the vapor/air mixture in the tank is flammable and explosive. As long as the tank is outbreathing through the PVV, the flame cannot pass from the low-pressure side through the PVV into the high-pressure side of the tank. However, extinguishment with dry chemical should be accomplished quickly to avoid flashback into the tank if heat damages the PVV. Reducing the pressure in the tank will extinguish the fire when the PVV closes. This can be accomplished by applying cooling water to the tank roof and shell. Maintain a positive pressure in the tank by introducing fuel gas. When a vapor-rich condition is indicated by the change of flame character, extinguishment can be accomplished with dry chemical.

Fighting Ground and Dike Fires Around Tanks

Extinguish all ground fires first. Apply cooling water as soon as possible to all flame-exposed metal. Close pertinent valves under the cover of water spray. Displace sufficient hydrocarbon with water to produce a water leak rather than a hydrocarbon fire. Water pressure must be greater than the hydrocarbon pressure in the tank. Do not overfill tank. Gain control of dike drains, roof drain, and water drain valves. When tanks that contain a high-flashpoint oil are exposed to ground fires, be aware of the possibility of a flammable mixture being created in the tank that can be ignited by the hot metal tank shell.

Vertical Atmospheric Tank Fires

Boilover occurs mostly with crude oil; there must be a major fire involving the entire liquid surface. Boilover occurs only in tanks with no floating roof. When crude oil burns, the light volatile fractions distill and burn off. The unvaporized hot (300F; 148.9C) residue, which is more viscous than the cold oil, begins to sink. As the fire progresses, the lighter fractions continue to distill at the interface between the hot residue layer and the cold crude oil. The burning vapor supplies the heat that continues the distillation. As the residue layer increases in depth, the interface moves downward two to three times faster than the burn-off rate at the oils surface. The hot residue is called the heat wave layer, and the interface is called the heat wave front. Crude oil tanks normally contain water or wet emulsion bottoms. As the hot interface reaches the water or emulsion in the bottom of the tank, it flashes the water into steam. At 400F (204.4C), water expands 2,000 times, to a frothy steam mixture. A good rule of thumb for the distance a boilover may travel is 10 times the diameter of the tank. Medium crudes are most likely to boil over. To estimate the time of a boilover, check the progress of the heat wave front by applying water to the tank shell, noting the location of the interface by the steam generated above the heat wave front. The heat wave front advances downward about 18 to 36 inches per hour. An imminent boilover is generally indicated by an increase in flame height and brightness. The best method to prevent boilover is to extinguish the fire rapidly. Foam application should begin within 30 minutes of ignition.

Slopover can result when a water stream is applied to the hot surface of burning oil, provided the oil is viscous and its temperature exceeds the boiling point of water. Since only the surface is involved, a slopover is a relatively mild occurrence.

Frothover means the overflowing of a tank not on fire when water or volatile hydrocarbons boil under the surface of viscous hot oil. An example would be when hot asphalt is loaded into a tank car that contains some water. The hot asphalt is cooled initially by contact with the cold metal. At first, nothing may happen; later the water can become superheated.

When it finally starts to boil, the asphalt may overflow the tank car. A similar situation can arise when a tank used for storing slops or residue at temperatures below 200F (93.3C) and containing a water bottom or wet emulsion receives a substantial addition of hot residue at a temperature above 212F (100C). After sufficient time has elapsed for the effect of the hot oil to reach the water in a tank, a prolonged boiling action can occur that can remove a tank roof and spread froth over a wide area.

Firefighting Agents

Water has the greatest heat-absorbing quality. It is used to cool equipment, structures, and tank shells that are exposed to fire and to prevent or reduce both heat damage and overpressure that result from overheating a vessel. When properly applied, it can extinguish hydrocarbon fires having a flashpoint above 100F. Water applied lightly to burning viscous liquids with flashpoints above 2,000F (1,093.3C) can produce a layer of froth on a liquid surface that acts like foam and smothers the fire. It can be used as a displacement medium in leaking hydrocarbon lines, or it may be used to float liquid hydrocarbons above a leak in a tank to interrupt product leakage. Water can be used effectively to control, but not extinguish, fires in low-flashpoint fuels.

Foam is used principally to form a cohesive floating blanket on the fuel surface that extinguishes the fire by smothering and cooling the fuel and prevents ignition by averting formation of combustible mixtures of vapor and air. Foams are particularly suited for extinguishing two-dimensional, flat, flammable liquid fires that involve spills or storage tanks. To achieve extinguishment of a tank fire or liquid fire of depth, however, continuous foam application at the required rate is critical. Unless the required rate of foam is applied and maintained on the liquid surface until a sealing, cohesive foam blanket is established, the fire will not be extinguished.

The formula for required rate of foam to extinguish a tank fire:

Surface area of tank = πr2

Solution required per sq. ft. = 0.16

Percent of concentrate being used = 0.03 or 0.06

Required application time = 30 or 60 minutes

πr2 · solution required per sq. ft. · percent of concentrate being used · total application time = total gallons of foam concentrate required to deliver the appropriate foam solution for 1 hour.

Example: 10,000 square foot tank

Step 1:

10,000 sq. ft. · 0.16 = 1,600 gallons per minute (gpm) of foam solution required.

Step 2:

1,600 gpm · 0.03 = 48 gallons of foam concentrate required per minute to produce 1,600 gpm.

Step 3:

48 gpm · 60 minutes = 2,880 gallons of concentrate required for a 1-hour application of 1,600 gpm of solution to extinguish a flammable liquid tank fire.

A 60-minute application rate is required for flammable liquids.

A 30-minute application rate is required for combustible liquids.

Subsurface Injection

The application rate for this technique is 0.1 gpm per square foot of surface area. The formula is the same as over-the-top delivery. High-back foam makers are required. The inlet velocity of foam into the tank is critical. In the case of flammable liquids, it should not exceed 10 feet per second. Combustibles will tolerate 20 feet per second. Subsurface injection is not recommended for internal or external floating roof tanks; it is recommended for cone roof tanks only.

Cooling Water

Cooling of adjacent tanks is usually unnecessary unless there is direct flame contact or sufficient radiant heat to scorch the paint. Check the temperature and heat absorption of a tank by applying water to its side to see if steam is produced. For best results, water should be fanned on the sides and roof; this does not, however, apply to roofs of floating roof tanks. Heat on the shells of tanks containing stocks, with an oil temperature above atmospheric temperature, may bring the vapor space of the tank within the flammable range. Heat on the shells of tanks containing low-flashpoint stocks may cause the tank pressure to rise and expel flammable vapors that may ignite or cause failure to the tank. A common error in tank firefighting is using too much cooling water on exposures. This can rob volume and water pressure from the water supply, and overtax sewers and drainage ditches, making firefighting difficult.

Dikes

Excessive water in a dike area can cause a leaking product to overflow the dike’s containment. Dikes should be monitored constantly during firefighting operations. Excessive water should be removed to another containment area until the fire is extinguished.

Activity 10.1:

Bulk Storage Facility/Tank Farm Simulation Exercise

Student Activity Worksheet

Time: 150 minutes (simulation and debrief) Purpose: To provide practice in using the ICS organization to manage an incident with extreme growth potential. Directions: - As a group, you will staff positions within the ICS of the Central City Fire Department (CCFD) for the exercise: - Incident Commander - Incident Commander Aide (not used unless nine students in a group) - Operations Chief - Operations Aide (a second Aide designated for groups with more than 10) - Planning Chief - Logistics Chief - Safety Officer - Information Officer - Liaison Officer - You will record all command decisions and actions during the exercise on the Simulation Action Chart. Entries on the ICS chart are made in response to written or visual messages or in anticipation of problems that could surface during the incident. Simulation outcomes: - Incident Commander: Team report - Operations Chief: Initial action plan and organizational chart - Operations Aide: Command worksheet, which includes objectives, strategies and tactics and an incident map - Planning Chief: Alternate plan - Logistics Chief: Resource list - Safety Officer: Safety message - Information Officer: Press release - At the conclusion of the exercise, all groups will participate in a debriefing facilitated by the instructors. Your group will display both the ICS charts and Simulation Action Charts that you developed during the exercise. Be prepared to explain your reasons for your decisions.

Incident overview: The incident occurs in a bulk storage facility that serves Central City and the surrounding area with a variety of petroleum products. It contains combustible and flammable liquids. The Beeline Oil Company is located at U and 6th Street. The incident begins on a Friday afternoon in July. The wind is gusting to 20 mph out of the southwest. At approximately 1635 hours, a thunderstorm moved through the area ahead of a front. Lightning struck the number 5 tank, which tore a hole 35’ x 6’ in the roof of the tank and ignited the product. It also opened a 15’ x 4’-hole at the rear of the tank. The remainder of the roof has been disfigured. Flames are visible on Sides B and D of the tank. - All tanks in dike area of the fire tank are internal floating roof tanks. - All tanks in adjacent dike area (Side B) are external floating roof tanks. - There are four tanks in each dike area. - Each internal floating roof tank has three foam chambers that may be pressurized outside the dike area. - All tanks in both dike areas are 48’ high x 100’ in diameter. - The water supply is from an 8-inch private hydrant system in the plant. The flow is 1,000 gpm. - The facility has a 1,000-gpm foam pumper with 500-gallon foam tank. - The plant has 500 gallons of foam in storage (5-gallon cans). - No tanks are set up for subsurface injection. If subsurface injection is used it will have to be improvised. Proper foam application rate: 1,256 gpm solution per minute for 1 hour. 37.68 gallons (3 percent) of foam concentrate per minute to support per-minute application. 2,220 gallons of foam concentrate to support 1-hour application. Incident priorities: - Life safety - Incident stabilization - Property conservation Strategies: - Rescue  Ventilation - Exposures  Salvage - Confinement - Extinguishment - Overhaul - Using the incident priorities and strategies, develop the control objectives. - Develop an incident organization. - Assign and manage resources.

Bulk Storage Facility/Tank Farm

Quick Access Fire Plan

| Building Address: U & 6th Street |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Building Description: Bulk storage plant--flammable and combustible materials Storage tanks 48' X 100' Cylindrical Roof Construction: Internal floating pan with cone roof External floater--external floating pan roof with wind girder Floor Construction: N/A |  |  |  |  |  |  |  |  |  |
| Occupancy Type: Bulk storage facility |  |  |  |  | Initial Resources Required: 1st alarm assignment |  |  |  |  |
| Hazards to Personnel: Flammable/Toxic materials |  |  |  |  |  |  |  |  |  |
| Location of Water Supply: 8-inch private yard system |  |  |  |  | Available Flow: 1,000-gpm hydrant |  |  |  |  |
|  |  | Estimated Fire Flow |  |  |  |  |  |  |  |
|  | Level of Involvement |  |  |  |  |  |  |  |  |
|  | Estimated Fire Flow |  |  |  |  |  |  |  |  |
| *Fire flow not determined for this facility type. |  |  |  |  |  |  |  |  |  |
| Fire Behavior Prediction: Flammable liquids characteristics |  |  |  |  |  |  |  |  |  |
| Predicted Strategies: Exposures--confinement—extinguishment |  |  |  |  |  |  |  |  |  |
| Problems Anticipated: Access to tanks: integrity of tank structure Water/Foam application |  |  |  |  |  |  |  |  |  |
| ¨ Standpipe: |  |  | ý Sprinklers: Foam chambers on tanks |  |  |  | ¨ Fire Detection: |  |  |

Central City Fire and Emergency Medical Services Fire Resources Overhead Positions—one Fire Chief, one Assistant Chief, one Chief Fire Marshal, seven Fire Inspectors, one Training Captain, two Training Lts., three Deputy Chiefs (1 per shift), six Battalion Chiefs (2 Battalions x 3 shifts). Eleven engine companies—Engines 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, and 11. Each engine company is staffed with one officer and three firefighters. Four truck companies—Trucks 1, 3, 5, and 8. Each truck company is staffed with one officer and three firefighters. Squad Company 1. The squad company is staffed with one officer and two firefighters fully trained in rescue practices. Crash/Fire/Rescue Engine. Airport-staffed with one officer and two firefighters. Engine 103, Engine 104, Engine 105, and Engine 109. Reserve Engines—fully equipped. Truck 103. Reserve Truck—fully equipped. Engine 104 (1,500-gpm foam pumper). Apparatus contains one 500-gallon foam tank; 400 five-gallon cans of foam are stored at Engine 4. All members of Engine 5 and Truck 5 have been fully trained as a Hazardous Materials Response Team. Mask Service Unit 106. Engine 206 (light truck). Boat 2 - 16’ Boston Whaler. EMS Resources (third service operated by the city and stationed in the fire stations): Three EMS supervisors – (one per shift x 3 shifts) operating out of fire station 1. Five ALS ambulances – ALS 2, 4, 7, 9, and 11 Five BLS ambulances – BLS 3, 5, 6, 8, and 10

Central City Fire/EMS Response Criteria 1st-Alarm Resource Card Response time: 5 min. Engine 1 Truck 1 Battalion 1 Engine 2 Ambulance 2 MSU 6 Engine 3 Squad 1 2nd-Alarm Resource Card Response time: 10 min. Engine 4 Truck 3 Battalion 2 Engine 5 Ambulance 3 Deputy Chief Engine 6 EMS Supervisor 3rd-Alarm Resource Card Response time: 15 min. Engine 7 Truck 5 Fire Marshal (Bn. Chief) Engine 8 Trng. Battalion Chief Engine 9 Adm. Battalion Chief 4th-Alarm Resource Card Response time: 15 min. Engine 10 Truck 8 Engine 11 5th-Alarm Resource Card Response time: 20 min. Fisherville Engine 1 Harvest Junct. Engine 2 Kingston Engine 1 6th-Alarm Resource Card Response time: 20 min. Apple Valley Engine 1 Bayport Engine 2 Jasper Engine 2 7th-Alarm Response Card Response time: 25 min. Deep Water Engine 2 Kingston Engine 3

Simulation Action Chart

MSSG.		TIME			ACTION TAKEN

Health and Safety Message

| Incident Name: |  | Date Prepared: |  |  | Time Prepared: |
| --- | --- | --- | --- | --- | --- |
| Operational Period Date: From: To: |  |  | Operational Period Time: From: To: |  |  |
| Major Hazards and Risks: |  |  |  |  |  |
| Narrative: |  |  |  |  |  |
| Prepared By; | Company Name: |  |  | ICS Position: Safety Officer |  |
| Approved By: | Company Name: |  |  | ICS Position: |  |

Press Questions

What are the contents of the tank that is on fire?

Will the fire spread to other tanks in the area?

Can a fire like this cause an explosion?

We have a report that the smoke coming from the fire is causing breathing problems to residents in the surrounding community. Is this true?

What should the residents do to avoid breathing the smoke?

Should the residents evacuate their homes? If so, where should they evacuate to?

Are the firefighters fighting the fire in any danger?

We have reports that some firefighters and plant personnel have been injured? Is this true?

How many firefighting resources are here?

How long will it be before the fire is controlled?

Activity 10.1:

Bulk Storage/Tank Farm Simulation Exercise

Student Assessment sheet

Debriefing: Debriefings are discussions centered on the cues contained in the written and visual messages, the strategies you developed as responses to the cues, and your organization and management of the incident staff. - What critical cues did you observe? - What ICS organization did you develop? - Did your group effectively prioritize responsibilities and actions? - Did you pass information to all who needed to be aware of it? - Did you promptly deal with messages? - Did you identify alternate methods of performing tasks? - Did you recognize the need for additional/outside resources? - Did you coordinate the allocation of resources? - Did you periodically re-evaluate resources? - How did your actions differ from the actions in the matrix? Why did they differ? - What are your strengths and weaknesses in working on an IMT for this incident? - How will you apply what you learned in this exercise to preplanning for a target hazard of this type in your community? - How will you apply what you learned in this exercise to responding to an incident at a target hazard of this type in your community?

Notes:

Module Summary

Managing a bulk storage facility/tank farm incident requires that you be particularly alert to strategies should the incident grow. Understanding the construction features of bulk storage facilities and tank farms, the types of tank farm fire, firefighting strategies, and resource requirements is a strong foundation to develop an effective ICS organization to manage an incident.